## Slide 1
New slopes for fan target
efficiency curves
---
A proposal based on a theoretical impeller efficiency and motor efficiencies according to IEC 60034-30 Ed 2.0

## Slide 2
Approach
In a first approach the progression of the fan target efficiency curve can be derived from the pure impeller efficiency depending on fluid dynamic laws and manufacturing demands and the motor efficiency requirements based on IEC 60034-30 Ed 2.0.
The derived impeller efficiency curve (brown line) is based on a scale-up considering the Reynolds-effect according to Ackeret (dotted line) combined with the assumption that the tip clearance grows linearly in practice from 0,5 % at Pe= 10kW to 1,0% at Pe=0,125 kW.
The fan efficiency curves resulting from the combination of impeller efficiency and motor efficiencies (IE3) are considerably lower than the requirement of the current regulation - especially for small fans.
With the new slopes this technical distortion can be corrected.
Note: This proposal is related exclusively to the shape (slopes) of the fan target efficiency curves, not to the absolute level!

## Slide 3
Derivation of new slopes
Chart: Power input, motor [kW]
| 0.12531725012293191 | 0.16332499957588065 | 0.23779723877449541 | 0.32299529902544738 | 0.46641848273050152 | 0.67768054537605338 | 0.90896930577478185 | 1.0007523127218581 | 1.3082133496615442 | 1.7588803561550068 | 2.5384406465930098 | 3.4201305194330529 | 4.5131121844071824 | 6.139812410194649 | 8.2928067213274144 | 10.000682269615494 | 12.03266049323441 | 16.279092090504967 | 19.978521213742631 | 23.666925877490467 | 32.067863831638604 | 39.394455838537382 | 47.748152133486791 | 58.168702579148452 | 78.960443291815182 | 94.524669250808628
Motor IE3_4P (IEC 60034-30) | 0.71818 | 0.73473 | 0.75695 | 0.77401 | 0.79328 | 0.81159 | 0.82511 | 0.82938 | 0.84084 | 0.85282 | 0.86667 | 0.87716 | 0.88631 | 0.89579 | 0.9044 | 0.90944 | 0.91418 | 0.92143 | 0.92599 | 0.92957 | 0.93552 | 0.93922 | 0.94244 | 0.94553 | 0.94984 | 0.95213
Motor IE3_2P (IEC 60034-30) | 0.65064 | 0.68476 | 0.71622 | 0.73983 | 0.76591 | 0.79006 | 0.80747 | 0.82725 | 0.84194 | 0.85853 | 0.87076 | 0.8812 | 0.89178 | 0.90117 | 0.90648 | 0.91158 | 0.91911 | 0.92378 | 0.9274 | 0.93334 | 0.93701 | 0.94018 | 0.9432 | 0.94745 | 0.94972
Motor IE3_6P (IEC 60034-30) | 0.64009 | 0.67117 | 0.70042 | 0.7228 | 0.748 | 0.77184 | 0.78937 | 0.80969 | 0.82509 | 0.84283 | 0.85619 | 0.8678 | 0.87977 | 0.89057 | 0.89641 | 0.90277 | 0.91175 | 0.91737 | 0.92175 | 0.92899 | 0.93346 | 0.93733 | 0.941 | 0.94609 | 0.94876
Impeller: scale-up considering Reynolds-effect by Ackeret | 0.53943 | 0.54026 | 0.54145 | 0.54242 | 0.54359 | 0.54477 | 0.5457 | 0.546 | 0.54685 | 0.54779 | 0.54895 | 0.54989 | 0.55077 | 0.55174 | 0.5527 | 0.55329 | 0.55387 | 0.55483 | 0.55548 | 0.55601 | 0.55698 | 0.55763 | 0.55824 | 0.55886 | 0.55983 | 0.5604
Impeller: scale-up considering Reynolds- and tip clearance effect | 0.49004 | 0.49385 | 0.49925 | 0.50365 | 0.50894 | 0.51431 | 0.51853 | 0.51991 | 0.52376 | 0.52802 | 0.53329 | 0.53758 | 0.54157 | 0.54599 | 0.55031 | 0.55301
Fan incl. motor IE3-4P | 0.35194 | 0.36285 | 0.37791 | 0.38983 | 0.40373 | 0.41741 | 0.42784 | 0.4312 | 0.4404 | 0.4503 | 0.46219 | 0.47154 | 0.47999 | 0.48909 | 0.4977 | 0.50292 | 0.50634 | 0.51124 | 0.51437 | 0.51685 | 0.52106 | 0.52373 | 0.52611 | 0.52842 | 0.53175 | 0.53357
Fan incl. motor IE3-2P | 0.31866 | 0.33886 | 0.35814 | 0.3731 | 0.39019 | 0.40664 | 0.41895 | 0.43348 | 0.44472 | 0.45796 | 0.46819 | 0.4773 | 0.48696 | 0.49597 | 0.50129 | 0.5049 | 0.50995 | 0.51314 | 0.51565 | 0.51985 | 0.5225 | 0.52484 | 0.52712 | 0.53041 | 0.53222
Fan incl. motor IE3-6P | 0.31364 | 0.33233 | 0.35047 | 0.36475 | 0.38131 | 0.39752 | 0.40981 | 0.42452 | 0.43605 | 0.44982 | 0.46057 | 0.47023 | 0.48058 | 0.49029 | 0.49572 | 0.50002 | 0.50587 | 0.50958 | 0.51251 | 0.51743 | 0.52052 | 0.52325 | 0.52589 | 0.52965 | 0.53168
Curve slopes (axial fans) 327/2011 | 0.37979 | 0.38705 | 0.39734 | 0.40573 | 0.4158 | 0.42604 | 0.43408 | 0.43672 | 0.44406 | 0.45217 | 0.46222 | 0.47039 | 0.47799 | 0.48643 | 0.49466 | 0.49979 | 0.5006 | 0.50296 | 0.50456 | 0.50588 | 0.50825 | 0.50985 | 0.51135 | 0.51289 | 0.51528 | 0.51668
Tip clearance 0,5%, > 10kW | 0.55301 | 0.55387 | 0.55483 | 0.55548 | 0.55601 | 0.55698 | 0.55763 | 0.55824 | 0.55886 | 0.55983 | 0.5604
Proposal new slopes (axial fans) | 0.32012 | 0.33286 | 0.35093 | 0.36565 | 0.38332 | 0.40129 | 0.41541 | 0.42003 | 0.42933 | 0.43962 | 0.45237 | 0.46272 | 0.47236 | 0.48305 | 0.4935 | 0.5 | 0.50269 | 0.50708 | 0.51006 | 0.51252 | 0.51694 | 0.51993 | 0.52273 | 0.52559 | 0.53004 | 0.53265

## Slide 4
Realistic impeller efficiency progression with new slopes
Chart: Power input, motor [kW]
| 0.12295677974008479 | 0.17524474240924973 | 0.25132101984103206 | 0.33791506372795932 | 0.48308332397122972 | 0.69614537662248155 | 0.92882322752756297 | 1.3297026743185529 | 1.7815944194173114 | 2.5625314792073048 | 3.4452714957564372 | 4.5392822092431286 | 6.1674180850446696 | 8.3225259983395343 | 10.000255151790567 | 12.067001280181127 | 16.320098657965371 | 20.026352795709851 | 23.722314926378555 | 32.142521952696946 | 39.487489279631134 | 47.863174145333751 | 58.311898985814203 | 79.159797409806259 | 94.764410838377515
Motor IE3_2P (IEC 60034-30) | 0.65064 | 0.68476 | 0.71622 | 0.73983 | 0.76591 | 0.79006 | 0.80747 | 0.82725 | 0.84194 | 0.85853 | 0.87076 | 0.8812 | 0.89178 | 0.90117 | 0.90648 | 0.91158 | 0.91911 | 0.92378 | 0.9274 | 0.93334 | 0.93701 | 0.94018 | 0.9432 | 0.94745 | 0.94972
Impeller: resulting from current slopes | 0.58293 | 0.56806 | 0.5569 | 0.55009 | 0.54414 | 0.54018 | 0.53832 | 0.53733 | 0.53748 | 0.53869 | 0.54044 | 0.54261 | 0.54559 | 0.54902 | 0.55136 | 0.54919 | 0.54725 | 0.54621 | 0.5455 | 0.54457 | 0.54415 | 0.54391 | 0.5438 | 0.54388 | 0.54405
Impeller: scale-up considering Reynolds- and tip clearance effect | 0.49004 | 0.49385 | 0.49925 | 0.50365 | 0.50894 | 0.51431 | 0.51853 | 0.51991 | 0.52376 | 0.52802 | 0.53329 | 0.53758 | 0.54157 | 0.54599 | 0.55031 | 0.55301
Impeller resulting fom proposal | 0.47512 | 0.47882 | 0.48441 | 0.49012 | 0.49811 | 0.50735 | 0.5153 | 0.51967 | 0.52268 | 0.52729 | 0.53169 | 0.53627 | 0.54185 | 0.54776 | 0.55159 | 0.5515 | 0.55175 | 0.55218 | 0.55268 | 0.55389 | 0.55492 | 0.55602 | 0.55728 | 0.55947 | 0.56089
Curve slopes (axial fans) 327/2011 | 0.37927 | 0.38898 | 0.39886 | 0.40697 | 0.41676 | 0.42678 | 0.43468 | 0.44451 | 0.45252 | 0.46248 | 0.47059 | 0.47815 | 0.48655 | 0.49476 | 0.49979 | 0.50063 | 0.50298 | 0.50458 | 0.5059 | 0.50827 | 0.50987 | 0.51137 | 0.51291 | 0.5153 | 0.5167
Tip clearance 0,5%, > 10kW | 0.55301 | 0.55387 | 0.55483 | 0.55548 | 0.55601 | 0.55698 | 0.55763 | 0.55824 | 0.55886 | 0.55983 | 0.5604
Proposal new slopes (axial fans) | 0.32012 | 0.33286 | 0.35093 | 0.36565 | 0.38332 | 0.40129 | 0.41541 | 0.42003 | 0.42933 | 0.43962 | 0.45237 | 0.46272 | 0.47236 | 0.48305 | 0.4935 | 0.5 | 0.50272 | 0.50716 | 0.51017 | 0.51266 | 0.51712 | 0.52014 | 0.52297 | 0.52587 | 0.53036 | 0.533

## Slide 5
Formulas for new slopes
1
10