## Slide 1: Background study for review of Fan Regulation 327/2011 2nd stakeholder meeting
René Kemna/ VHK
Brussels, 22 January 2015

## Slide 2: Draft agenda
10:00 Start meeting Welcome and introduction 10:10 - 13:00 Part 1 discussion document (mainly text)
Article 1 Scope
Article 2 Definitions
Article 3 Reference to Annex II (+ allowances dual use/reversible/ATEX)
Annex I Technical definitions
13:00 - 14:00 Lunch 14:00 - 17:00 Part 2 discussion document (mainly figures)
Annex II Ecodesign requirements (slopes, targets)
Annex III Product information
Annex IV Verification
Annex V Benchmarks
17:00-17:30 AOB
meeting will be recorded

## Slide 3: Background
327/2011, Recital 14:
  consider setting technology independent requirements, potential of use of VSD, reduce exemptions, consider fans below 125 W
Article 7:
  review of Regulation no later than 4 years (6 months to CF meeting, 30 March 2015)
  assess feasibility of reducing number of fan types
  can scope of exemptions be reduced, including allowances for dual use fans
plus other relevant issues / topics
  jet fans, replacement fans, etc.

## Slide 4: Study objectives
Tasks:
  reduction of fan types possible?
  reduction of exemptions possible?
  assess adequacy of allowance for dual use fans
  requirements for jet fans? (plus impacts)
  assess adequacy of market surveillance
  other information relevant for review (impact 327/2011?)
Website www.fanreview.eu , email list

## Slide 5: Time path
Activity | Month |  |  |  |  |  |  |  |  |  |  |  |  |  | 
month | 0 | +1 | +2 | +3 | +4 | +5 | +6 | +7 | +8 | +9 | +10 | +11 | +12 | ... | +18
indicative month | Apr '14 | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan '15 | Feb | Mar | Apr | ... | Oct
Reporting |  |  |  | 1st IR |  |  |  | disc. docs |  | 2nd IR | 2nd IR |  |  |  | FR
Other activities |  | kick-off website |  |  |  | 1st SH meeting |  |  | 2nd SH meeting | 2nd SH meeting |  | CF meeting? |  | technical assistance | 
IR = Interim report (1+2): 1st report sent 1 Aug. 2014, available on www.fanreview.eu from 4 Sept. 2014
Discussion docs = Published 21 Nov. 2014 on website
FR = Final Report
SH = Stakeholder meeting s(1+2) 1 Oct. 2014, 22 Jan. 2015
CF = Consultation Forum meeting (indicative)

## Slide 6: Discussion document 21.11.2014 Article 1.1
Article 1 | Article 1
Subject matter and scope | Subject matter and scope
1. This Regulation establishes ecodesign requirements for the placing on the market or putting into service of fans, including those integrated in other energy-related products as covered by Directive 2009/125/EC. | 1. This Regulation establishes ecodesign requirements for the placing on the market or putting into service of fans with an end-use as component or as sub-assembly integrated in other products.

## Slide 7: Article 1.1 intention (legal text later..)
Motor package
Rotor +Stator
Product + fan (final stator?)
Rotor & Stator & Product
Motor&
Rotor & Stator & Product
DoC
DoC
fantest
fantest
CE-motor
CE-fan
CE-product
Customer
End-Manufacturer
Fan OEM
Motor OEM
Motor package
Default* (orifice)
Final* stator
or
DoC
fantest
Motor+ Rotor + Stator
Product + fan
fantest
DoC
CE-motor
CE-fan
CE-product
CE-motor
CE-fan
CE-product
CE-motor
CE-fan
CE-product
All tests in accordance with ISO 5801
(with orifice panel or final stator design)

## Slide 8: Article 1.2
2. The Regulation shall not apply to fans integrated in: | 2. The Regulation shall not apply to fans integrated in:
(i) products with a sole electric motor of 3 kW or less where the fan is fixed on the same shaft used for driving the main functionality; | (i) products with a sole electric motor of 3 kW or less where the fan is used for motor cooling only and fixed on the same shaft used for driving the main functionality;
(ii) laundry and washer dryers ≤ 3 kW maximum electrical input power; | (ii) laundry and washer dryers ≤ 3 kW maximum electrical input power;
(iii) kitchen hoods < 280 W total maximum electrical input power attributable to the fan(s). | (iii) kitchen hoods < 280 W total maximum electrical input power attributable to the fan(s).
 | (iv) with a best energy efficiency point (bep) at 8 000 rotations per minute or more;

## Slide 9: Article 1.2 considerations for exemptions
Fan producers: No exemptions, esp. not for hoods and drier fans that are not extraction or circulation fans
Fan buyers: Exemptions for all ED-regulated products (double regulation…)
Cooling fan producers: Stator unknown (e.g. cooling tower) and end-user cannot test: ask exemption for their fans or (Multi-Wing) alternative (next slide)
Current Reg: Specific exceptions
Discussion doc: Specific exceptions with improved definitions (2 extra exceptions: nuclear power and RH>90%)
Discussion doc cooling fan: If stator is unknown, then fans can be tested with default stator (orifice panel cf. ISO 5801) and no new test by end-user is needed to be in conformity with fan regulation. Same as today… If needed a specific mandate for more useful cooling fan testing could be issued by the EC.

## Slide 10: Article 1.2 alternative test (default stator)
Orifice panel (cf ISO 5801)
Direct drive
Belt drive
Application
Compliance test

## Slide 11: Article 1.3 a), b)
3. This Regulation shall not apply to fans which are: | 3. This Regulation shall not apply to fans which are specified to operate exclusively:
(a) designed specifically to operate in potentially explosive atmospheres as defined in Directive 94/9/EC of the European Parliament and of the Council (1); | (moved to later in Art. 3)
(b) designed for emergency use only, at short-time duty, with regard to fire safety requirements set out in Council Directive 89/106/EC (2); | (a) for emergency use only, at short-time duty of 1 hour or more, with regard to fire safety requirements for temperatures of 300°C and above set out in Regulation (EU) No 305/2011 of the Council and the Parliament.
 | (b) in nuclear power plants

## Slide 12: Article 1.3 considerations for exemptions
3 a) As discussed in 1st SH meeting: only F300 and above (not F200). ‘1 hour or above’ to be stricken?
New exemption: Nuclear power plants (reference to specific legislation to be added)
ATEX  see Art. 3.4

## Slide 13: Article 1.3 c) to g)
(c) designed specifically to operate: | 
(i) (a) where operating temperatures of the gas being moved exceed 100 °C; | (c) where operating temperatures of the gas being moved exceed 100 °C;
(b) where operating ambient temperature for the motor, if located outside the gas stream, driving the fan exceeds 65 °C; | (d) where operating ambient temperature for the motor, if located outside the gas stream, driving the fan exceeds 60 °C;
(ii) where the annual average temperature of the gas being moved and/or the operating ambient temperature for the motor, if located outside the gas stream, are lower than – 40 °C; | (e) where the annual average temperature of the gas being moved and/or the operating ambient temperature for the motor, if located outside the gas stream, are lower than – 30 °C;
(iii) with a supply voltage > 1 000 V AC or > 1 500 V DC; | (f) with a supply voltage > 1 000 V AC or > 1 500 V DC;
(iv) in toxic, highly corrosive or flammable environments or in environments with abrasive substances; | (g) handling toxic, highly corrosive or flammable gases or vapours as set out in Regulation (EC) No 1272/2008 and its adaptations;

## Slide 14: Article 1.3 considerations for exemptions
3 d) & e) temperatures consistent with draft motor regulation. Ebmpapst likes to keep 65° and not 60°(keep more cooling fans in the scope)
3 f) Regulation (EC) No 1272/2008 and its adaptations (CLP) gives a comprehensive overview of 1353 pages, making absolutely clear (in a dispute) what are ‘toxic, highly corrosive or flammable gases or vapours’ and at what concentrations
Eurovent feels that the reference to CLP regulation does not help…

## Slide 15: Article 1.3 h) to m)
 | (h) handling abrasive substances with a hardness of at least 5 Mohs with a concentration of at least 100 mg/m³;
 | (i) handling gases containing biohazardous substances of risk groups 2, 3 and 4 as set out in Regulation (EC) 2000/54/EC
Art. 3, 4, (c) [ ..shall not apply to…] as conveying fans used for the transport of non-gaseous substances in industrial process applications. | (j) handling gases with a solid particle concentration of more than 200 mg/m³ and/or particles with an average diameter of 1 mm;
 | (k) handling gases with a compressibility factor, rounded to the nearest 2 decimal places, in the designated pressure and temperature range of the scope that is not equal to 1,00;
 | (l) in cordless or battery operated equipment;
 | (m) in hand-held equipment whose weight is supported by hand during operation;

## Slide 16: Article 1.3 considerations for exemptions
3 h) to j) clearer define what is abrasive, biohazardous or solids (including conveyor functionality)
3 k) Means that the compressibility factor is between 0.995 and 1.005, which means that (as opposed to the old Annex II) the compressibility factor does not need to be taken into account (=1).
3 l) and m): taken from the draft motor regulation for reasons of consistency.

## Slide 17: Article 1.3 n) and closing
(d) placed on the market before 1 January 2015 as replacement for identical fans integrated in products which were placed on the market before 1 January 2013; except that the packaging, the product information and the technical docu­mentation must clearly indicate regarding (a), (b) and (c) that the fan shall only be used for the purpose for which it is designed and regarding (d) the product(s) for which it is intended. | (n) as a replacement for identical fans that are no longer compliant with the minimum requirements in this regulation, for a period of 5 years after the implementation date of the tier whose requirements could not be met by the identical fan to be replaced;
 | whereby the packaging, the product information and the technical docu­mentation must clearly indicate regarding (a) to (m) that the fan shall only be used for the purpose for which it is specified and regarding (n) the product(s) for which it is intended.

## Slide 18: Article 1.3 considerations for exemptions
3 l) to be replaced by new exemption: ‘handling gases and vapours with a relative humidity larger than 90%’ (to accomodate extraction fans from evaporative cooling towers)
All the rest shifts  3 n) becomes 3 o):
The period of 5 years to be able to replace fans, after they are phased out, is in line with the period in existing Ecodesign regulations (regulators, circulators).

## Slide 19: Article 2.1
Article 2 | Article 2
Definitions | Definitions
In addition to the definitions set out in Directive 2009/125/EC, the following definitions shall apply: | In addition to the definitions set out in Directive 2009/125/EC, the following definitions shall apply:
1. ‘Fan’ means a rotary bladed machine that is used to maintain a continuous flow of gas, typically air, passing through it and whose work per unit mass does not exceed 25 kJ/kg, and which: | 1. ‘Fan’ means a configuration of impeller, stator, electric motor, transmission or direct drive and possibly a variable speed drive, intended for the continuous displacement of gas with at its bep an electric input power between 125 W and 500 kW (≥ 125 W and ≤ 500 kW), a pressure-increase ratio lower than 1.1 and an output air velocity lower than 51,5 m/s, and which is an axial fan, centrifugal fan, cross flow fan, mixed flow fan or jet fan.

## Slide 20: Article 2.1 considerations for definitions
Industry prefers ‘motor package’ to define the combination of motors and drive (incl. VSD) extra definition but no problem (Q: includes also power supply for DC?)
a pressure-increase ratio lower than 1.1  delineation with compressors (consistent with draft compressor regulation)
..and an output air velocity lower than 51,5 m/s  Mach factor is lower than 0.15 and thus (cf. ISO 5801) needs not to be taken into account (simplification of current regulation, Annex II)
Electric power input to define scope is not normal; usually power output (e.g. air power, Δp * qv, between 50 W and 400 kW)
The description of fan types was added to have a more compact tekst (already many definitions)

## Slide 21: Article 2.2 (and 2.3)
 | 2. ' bep' is the best energy efficiency point for fan operation, as declared by the manufacturer and specified by the applicable fan speed, expressed in rounds per minute (rpm);
— is designed for use with or equipped with an electrical motor with an electric input power between 125 W and 500 kW (≥ 125 W and ≤ 500 kW) to drive the impeller at its optimum energy efficiency point, | Included above
— is an axial fan, centrifugal fan, cross flow fan or mixed flow fan, | included above
— may or may not be equipped with a motor when placed on the market or put into service; | no longer applicable
2. ‘Impeller’ means the part of the fan that is imparting energy into the gas flow and is also known as the fan wheel; | 3. ‘Impeller’ means the part of the fan that is imparting energy into the gas flow and is also known as the fan wheel;

## Slide 22: Article 2.2 considerations for definitions
‘bep’ is shorter and also more common than ‘optimum energy efficiency point’.
Question from standardisation (Brivio): Should it be defined at the declared ‘maximum’ speed (=speed beyond which manufacturer assumes no liability) or any point is allowed?
Question for (probably) future standardisation: Fans use strict product approach (max. speed with different resistance to define operating point), like motors and VUs, but circulators, pumps, RACs use extended product approach (different rpm points to define part load, as is common for motor+VFD). Covered by Mandate 500 (System Efficiency matrix)?

## Slide 24: Article 2.4 – 2.6
moved from Annex II -> | 4. ‘Stator’ is the stationary part of the fan which interacts with the air stream passing through the impeller and, within the geometrical air-stream envelope between defined fan inlet- and outlet sections, includes any part that may increase, and excludes any non-fan component that may decrease, the fan efficiency, following manufacturer's instruction. Instead of the stator-component that is part of the product placed on the market, the manufacturer may use a geometrical equivalent (or a default orifice panel)
moved from Annex II -> | 5. ‘Transmission’ means a driving arrangement for a fan which is not ‘direct drive’ as defined above. Such driving arrangements may include transmissions using a belt-drive, gearbox or slipping coupling.
moved from Annex II -> | 6. ‘Direct drive’ means a driving arrangement for a fan where the impeller is fixed to the motor shaft, either directly or with a co-axial coupling, and where the impeller speed is identical to the motor’s rotational speed.

## Slide 25: Article 2.4-2.6 considerations for definitions
The definition of ‘stator’ is derived from work-in-progress of TC156/WG17, the ISO 5801 test conditions (require a definition of ‘inlet’ and ‘outlet’) and takes into account that the fan may be a self-standing product or a set of components inside another product.
‘any part that may increase…fan efficiency’: guide vanes, diffusers, inlet/outlet bell or inlet cone and --possibly (manufacturer decides..)– silencers/attenuators (not always bad)
‘any part that may decrease…fan efficiency’: fan guards, motor grids, shutters, deflectors, rain protection, integrated heaters/coolers/heat recovery devices, filters and filter casings, sensors, valves, dampers, stepper motors and –possibly (manufacturer decides..)– silencers/attenuators.

## Slide 26: Article 2.6/2.7
6. ‘Variable speed drive (VSD)’ means an electronic power converter integrated — or functioning as one system — with the motor and the fan, that continuously adapts the electrical power supplied to the electric motor in order to control the mechanical power output of the motor according to the torque-speed characteristic of the load being driven by the motor, excluding variable voltage controllers where only the supply voltage for the motor is varied. | 7. ‘Variable speed drive (VSD)’ ‘variable speed drive (VSD)’ means an electronic power converter, integrated or functioning as one system or as a separate delivery with the motor and the fan, which continuously adapts the electrical power supplied to the motor in order to control its mechanical power output according to the torque-speed characteristic of the load it is driving, including EC (electronically commutated) motors with an internal control, excluding variable voltage controllers where only the supply voltage for the motor is varied;

## Slide 27: Article 2.4-2.6 considerations for definitions
VSD definition extended to also include EC motor regulation and not only VFD. (text taken from VU regulation)

## Slide 28: Article 2.8
 | 7. The ‘specific pressure ratio’ means the stagnation pressure measured at the fan outlet divided by the stagnation pressure at the fan inlet at nominal flow rate.
3. ‘Axial fan’ means a fan that propels gas in the direction axial to the rotational axis of one or more impeller(s) with a swirling tangential motion created by the rotating impeller(s). The axial fan may or may not be equipped with a cylindrical housing, inlet or outlet guide vanes or an orifice panel or orifice ring; | 8. ‘Axial fan’ means a fan that propels gas in the direction axial to the rotational axis of one or more impeller(s) with a swirling tangential motion created by the rotating impeller(s).
4. ‘Inlet guide vanes’ are vanes positioned before the impeller to guide the gas stream towards the impeller and which may or may not be adjustable; | definition not used (deleted)
5. ‘Outlet guide vanes’ are vanes positioned after the impeller to guide the gas stream from the impeller and which may or may not be adjustable; | definition not used (deleted)

## Slide 29: Article 2.8 considerations for definition fan types
Problem: Ambiguous definition of fan types (in current reg.). Possible alternatives? (also from TC156/WG17):
±20°
±20°
± 70°
± 20°
AXIAL
CENTRIFUGAL
MIXED FLOW
CROSS-FLOW
Inlet and outlet parallel to the rotor axis ±20°
Inlet parallel to and outlet perpendicular to the rotor axis ±20°
Inlet parallel to and outlet at an angle of 45° ±25° to the rotor axis
Inlet and outlet air at circumference of the rotor at any angle

## Slide 30: Article 2.9
6. ‘Orifice panel’ means etc; | definition not used (deleted)
7. ‘Orifice ring’ means a ring with an opening in which the fan sits and which allows the fan to be fixed to other structures; | 
8. ‘Centrifugal fan’ means a fan in which the gas enters the impeller(s) in an essentially axial direction and leaves it in a direction perpendicular to that axis. The impeller may have one or two inlets and may or may not have a housing; | 9. ‘Centrifugal fan’ means a fan in which the gas enters the impeller(s) in an essentially axial direction and leaves it in a direction perpendicular to that axis.
9. ‘Centrifugal radial bladed fan’ means a centrifugal fan where the outward direction of the blades of the impeller(s) at the periphery is radial relative to the axis of rotation; | definition not used (deleted)
10. ‘Centrifugal forward curved fan’ means a centrifugal fan where the outward direction of the blades of the impeller(s) at the periphery is forward relative to the direction of rotation; | definition not used (deleted)

## Slide 31: Article 2.10
11. ‘Centrifugal backward curved fan without housing’ means a centrifugal fan where the outward direction of the blades of the impeller(s) at the periphery is backward relative to the direction of rotation and which does not have a housing; | definition not used (deleted)
12. ‘Housing’ means a casing around the impeller which guides the gas stream towards, through and from the impeller; | replaced by ‘stator’
13. ‘Centrifugal backward curved fan with housing’ means a centrifugal fan with an impeller where the outward direction of the blades at the periphery is backward relative to the direction of rotation and which has a housing; | definition not used (deleted)
14. ‘Cross flow fan’ means a fan in which the gas path through the impeller is in a direction essentially at right angles to its axis both entering and leaving the impeller at its periphery; | 10. ‘Cross flow fan’ means a fan in which the gas path through the impeller is in a direction essentially at right angles to its axis both entering and leaving the impeller at its periphery;

## Slide 32: Article 2.11
15. ‘Mixed flow fan’ means a fan in which the gas path through the impeller is intermediate between the gas path in fans of centrifugal and axial types; | 11. ‘Mixed flow fan’ means a fan in which the gas path through the impeller is intermediate between the gas path in fans of centrifugal and axial types;
16. ‘Short-time duty’ means working of a motor at a constant load, which is not long enough to reach temperature equilibrium; |  not needed (included in art. 1)
17. ‘Ventilation fan’ means a fan that is not used in the following energy-related products: | no longer applicable
— laundry and washer dryers > 3 kW maximum electrical input power, | 
— indoor units of household air-conditioning products and indoor household air-conditioners, ≤ 12 kW maximum airco output power, | 
— information technology products; | 
18. The ‘specific ratio’ means the stagnation pressure measured at the fan outlet divided by the stagnation pressure at the fan inlet at the optimal energy efficiency point of the fan. | moved upwards (Art. 1)

## Slide 33: Article 2.12
new test standard available Comment: drop ‘axial’ (also centrifugal) ISO/DIS 13350:2014 'Fans — Performance testing of jet fans' (first voting is approved, final voting and procedural steps to follow). | 12. ' Jet fan' means an axial fan used for producing a jet of air in a space and unconnected to any ducting, for which an alternative test and calculation method applies based on the measured thrust.

## Slide 34: Article 2.12 considerations for definitions
The ISO/DIS standard does not contain a complete definition of jet fans. Comment industry: ‘jet fan’ can also be centrifugal (so drop ‘axial’?).
Basically there is no alternative to self-declaration (?).

## Slide 35: Article 3 (3.1-3.3)
Ecodesign requirements | Ecodesign requirements
1. The ecodesign requirements for fans are set out in Annex I. | 1. The ecodesign requirements for fans are set out in Annex II.
2. Each fan energy efficiency requirement of Annex I Section 2 shall apply in accordance with the following timetable: | 2. Each fan energy efficiency requirement of Annex II shall apply in accordance with the following timetable:
(a) first tier: from 1 January 2013, ventilation fans shall not have a lower target energy efficiency than as defined in Annex I, Section 2, Table 1; | (a) first tier: from 1 January 2018, all fans shall not have a lower target energy efficiency than as defined in Annex II, Table 1;
(b) second tier: from 1 January 2015, all fans shall not have a lower target energy efficiency than as defined in Annex I, Section 2, Table 2. | (b) second tier: from 1 January 2020, all fans shall not have a lower target energy efficiency than as defined in Annex II, Table 1.
3. The product information requirements on fans and how they must be displayed are as set out in Annex I, Section 3. These requirements shall apply from 1 January 2013. | 3. The product information requirements on fans and how they must be displayed are as set out in Annex III. These requirements shall apply from 1 January 2018.

## Slide 36: Article 3 considerations for requirements
References in discussion document were corrected (Annex II and III in the new structure)
Next slide: These exemptions no longer apply or are moved to Art. 1

## Slide 37: Article 3.4 (eliminated)
4. The fan energy efficiency requirements of Annex I Section 2 shall not apply to fans which are designed to operate: | 4. The fan energy efficiency requirements of Annex I Section 2 shall not apply to fans which are designed to operate:
(a) with an optimum energy efficiency at 8 000 rotations per minute or more; |  already in Art. 1
(b) in applications in which the ‘specific ratio’ is over 1,11; |  already in fan definition (should be 1.1)
(c) as conveying fans used for the transport of non-gaseous substances in industrial process applications. |  addressed in Art. 1

## Slide 38: Article 3.4(new)-3.6
5. For dual use fans designed for both ventilation under normal conditions and emergency use, at short-time duty, with regard to fire safety requirements as set out in Directive 89/106/EC, the values of the applicable efficiency grades set out in Annex I Section 2 will be reduced by 10 % for Table 1 and by 5 % for Table 2. | 4. For dual use fans designed for both ventilation under normal conditions and emergency use as set out in Art. 1, 3 (a), the values of the applicable efficiency grades set out in Annex I Section 2 will be reduced by 5 %.
ATEX fans (moved from Art. 1) | 5. For fans designed specifically to operate in potentially explosive atmospheres as defined in Directive 94/9/EC of the European Parliament and of the Council (1), the values of the applicable efficiency grades set out in Annex I Section 2 will be reduced by 10 %.
6. Compliance with ecodesign requirements shall be measured and calculated in accordance with requirements set out in Annex II. | 6. Compliance with ecodesign requirements shall be measured and calculated in accordance with requirements set out in Annex II.

## Slide 39: Article 3.4-3.6 considerations for requirements
Dual use also includes reversible fans (why else would they be reversible if not in case of fire). Make explicit? Make definition!
In 1st SH meeting some said 6-10% allowance, some said no allowance needed for dual use. Proposal is 5%. EVIA: More. FW: at least 10% (F300) and more for higher class.
ATEX fans are excluded in current fan regulation, but in draft motor regulation they are (probably) not. Should be consistent. Proposal 10% allowance. Eurovent: More.
The 5% and 10% allowance relate to a discount on the minimum values (=factor 0.95 and 0.9 times ηmin). They are not N-percentage points (as is also the case in the current regulation)

## Slide 40: Articles 4, 5, 6, 8 (no change)
Article 4 : Conformity assessment | Article 6: Indicative benchmarks
The conformity assessment procedure referred to in Article 8 of Directive 2009/125/EC shall be the internal design control system set out in Annex IV to that Directive or the management system for assessing conformity set out in Annex V to that Directive. | The indicative benchmarks for the best-performing fans available on the market at the time of entry into force of this Regulation are set out in Annex IV.
Article 5: Verification procedure for market surveillance purposes | Article 8: Entry into force
When performing the market surveillance checks referred to in Article 3(2) of Directive 2009/125/EC, the authorities of the Member States shall apply the verification procedure set out in Annex III to this Regulation. | This Regulation shall enter into force on the 20th day following its publication in the Official Journal of the European Union.

## Slide 41: Article 7
Article 7 | Article 7
Revision | Revision
The Commission shall review this Regulation no later than 4 years after its entry into force and present the result of this review to the Ecodesign Consultation Forum. The review shall in particular assess the feasibility of reducing the number of fan types in order to reinforce competition on grounds of energy efficiency for fans which can fulfil a comparable function. The review shall also assess whether the scope of exemptions can be reduced, including allowances for dual use fans. | The Commission shall review this Regulation no later than 5 years after its entry into force in the light of technological progress. The review will include the assessment of design options that can facilitate re-use and recycling. The results of this review shall be presented to the Ecodesign Consultation Forum.

## Slide 42: Annexes

## Slide 43: Annex I.1, (1) to (5)
(1) ‘Measurement category’ means a test, measurement or usage arrangement that defines the inlet and outlet conditions of the fan under test. | (1) ‘Measurement category’ means a test, measurement or usage arrangement that defines the inlet and outlet conditions of the fan under test.
(4) ‘Measurement category A’ means an arrangement where the fan is measured with free inlet and outlet conditions. | (2) ‘Measurement category A’ means an arrangement where the fan is measured with free inlet and outlet conditions.
(5) ‘Measurement category B’ means an arrangement where the fan is measured with a duct fitted to its inlet and outlet. | (3) ‘Measurement category B’ means an arrangement where the fan is measured with a duct fitted to its inlet and outlet.
(4) ‘Measurement category C’ means an arrangement where the fan is measured with free inlet conditions and a duct fitted to its outlet | (4) ‘Measurement category C’ means an arrangement where the fan is measured with free inlet conditions and a duct fitted to its outlet
(5) ‘Measurement category D’ means an arrangement where the fan is measured with a duct fitted to its inlet and outlet. | (5) ‘Measurement category D’ means an arrangement where the fan is measured with a duct fitted to its inlet and outlet.

## Slide 44: Annex I considerations for definitions
These measurement categories are here to make an implicit link to ISO 5801 and thus are kept. Otherwise it could be defined more compact.

## Slide 45: Annex I.1, (6)
(6) ‘Efficiency category’ means the fan gas output energy form used to determine the fan energy efficiency, either static efficiency or total efficiency, where: | (6) ‘Efficiency category’ means the fan gas output energy form used to determine the fan energy efficiency, with a distinction between 'static', 'dynamic' or 'total' efficiency depending on whether the fan gas power has been determined with respectively the static, dynamic or total pressure difference between fan in- and outlet;
(a) ‘fan static pressure’ (psf) has been used to determine fan gas power in the efficiency equation for fan static efficiency; and |  already included in (6)
(b) ‘fan total pressure’ (pf) has been used to determine fan gas power in the efficiency equation for total efficiency. |  already included in (6)

## Slide 46: Annex I.1, (7)
(7) ‘Static efficiency’ means the energy efficiency of a fan, based upon measurement of the ‘fan static pressure’ (psf). Taken from Annex II, section 3.1  | (7) ‘Fan efficiency’ (ηf) is the ratio of the fan gas power output Pu and the electric power input Pe, both expressed in W and determined at bep, multiplied with correction factors for power conversion Cp and part load compensation Cc, following the expression ηf = Cp∙Cc∙Pu/Pe , with a distinction between 'static', 'dynamic' or 'total' efficiency depending on whether the fan gas power has been determined with respectively the static, dynamic or total pressure difference between fan in- and outlet;

## Slide 47: Annex I considerations for definitions
These definitions in previous and 2 following slides are a more compact version of the current Annex II, section 3.1, but
The addition of the power conversion correction factor (0.9, applies to DC fans, defined later) is new. It is included to create a level playing field for those applications where there is a choice between DC and AC motors.

## Slide 48: Annex I.1, (8) & (9)
taken from Annex II, section 3.1 | (8) 'Fan gas power' Pu, in W, is the product of the fan volume flow rate qv, in m³/s, and the pressure difference between fan in- and outlet Δp, in Pa, both determined at bep, following the expression Pu= qv∙Δp, with a distinction between 'static', 'dynamic' or 'total' fan gas power depending on whether the fan gas power has been determined with respectively the static, dynamic or total pressure difference Δp between fan in- and outlet;
taken from Annex II, section 3.1 | (9) 'Electric power input' Pe, in W, is the electric input power at bep, measured at main terminals of motor or, when present, variable speed drive;

## Slide 49: Article I.1, (10)
 | (10) 'Power conversion correction' Cp, is a correction factor for power conversion losses with a default value of 0.9 for fans using DC current with a voltage lower than 100 V;
taken from Annex II | (11) 'Part load compensation' Cc is a correction factor with one of the following values: — Cc=1 for a motor without a variable speed drive, — Cc=1,04 for a motor with a variable speed drive and Pe ≥ 5 kW, — Cc = – 0,03 ln(Pe) + 1,088 for a motor with a variable speed drive and Pe < 5 kW;

## Slide 50: Annex I.1, (12-14)
 | (12) 'Fan flow rate' qv, in m³/s, is the gas volume displaced per unit of time by the fan and is typically derived from assessment of the fan dynamic pressure difference, air velocity or measured thrust, calculated using the gravitational gas density ρ at default 1.2 kg/m³ and the fan outlet surface area;
(8) ‘Fan static pressure’ (psf) means the fan total pressure (pf) minus the fan dynamic pressure corrected by the Mach factor. | (13) 'Fan static pressure' (pfs), in Pa, is the omnidirectional force per unit surface area exerted at the fan outlet and is typically assessed by measuring the stagnation pressure in a (cylindrical) hole of appropriate geometry and dimensions, in duct wall or appropriate measurement instrument perpendicular to the direction of the gas flow.
(10) ‘Dynamic pressure’ means the pressure calculated from the mass flow rate, the average gas density at the outlet and the fan outlet area. | (14) 'Fan dynamic pressure' (pfd), in Pa, is the pressure derived from the kinetic energy of the fan, also known as 'velocity pressure', and is typically assessed from the difference between total and static pressure or, for jet fans, by measuring the reactive thrust force Tm, in N, excerted on the fan by the gas flow and dividing by the fan outlet surface area A2, in m².

## Slide 51: Annex I considerations for definitions
The definitions for flow rate (qv), fan static pressure (pfs), fan dynamic pressure (pfd) and fan total pressure (pf) are new, because the existing definitions are unclear; i.e. they assume specific knowledge of ISO 5801 and stagnation pressure e.g. a Pitot-static tube in testing (see figure)
Total pressure pf − Static pressure pfs = dynamic pressure pfd
pressure p
air velocity v
density ρ = 1.2
pressure gauge (transducer)
pfs
pf
Lateral opening (v=0)
Pitot tube
Stagnation pressure is pressure measured at the end of pitot-tube

## Slide 52: Annex I considerations for definitions: Jet fan
Comment industry: For jet fan we should use the definition in the ISO/DIS standard. Question VHK: What is the definition exactly, total or dynamic?

## Slide 53: Annex I considerations for definitions: Jet fan (c’td)
Thrust meter
Thrust Tm

## Slide 54: Annex I.1, (15)
(11) ‘Mach factor’ means a correction factor applied to dynamic pressure at a point, defined as the stagnation pressure minus the pressure with respect to absolute zero pressure which is exerted at a point at rest relative to the gas around it and divided by the dynamic pressure. |  no longer needed because v< 51,5 m/s (see Art. 2)
(12) ‘Total efficiency’ means the energy efficiency of a fan, based upon measurement of the ‘fan total pressure’ (pf ). |  included in (6)
(13) ‘Fan total pressure’ (pf ) means the difference between the stagnation pressure at the fan outlet and the stagnation pressure at the fan inlet. | (15) 'Fan total pressure' (pf), in Pa, is the directional force per unit surface area exerted at the fan outlet and is typically assessed by measuring the stagnation pressure in a (cylindrical) hole of appropriate geometry dimensions facing the direction of the gas flow or for jet fans by measuring the reactive thrust force exerted on the fan by the gas flow per unit fan outlet surface area.

## Slide 55: Annex I, (16-18)
(9) ‘Stagnation pressure’ means the pressure measured at a point in a flowing gas if it were brought to rest via an isentropic process. | (16) ‘Stagnation pressure’ means the pressure measured at a point in a flowing gas if it were brought to rest via an isentropic process.
(14) ‘Efficiency grade’ is a parameter in the calculation of the target energy efficiency of a fan of specific electric input power at its optimum energy efficiency point (expressed as parameter ‘N’ in the calculation of the fan energy efficiency). | (17) ‘Efficiency grade’ is a parameter in the calculation of the minimum fan efficiency at specific electric input power at its bep (expressed as parameter ‘N’ in the calculation of the minimum fan efficiency).
(15) The ‘target energy efficiency’ (ηtarget) is the minimum energy efficiency a fan must achieve in order to meet the requirements and is based on its electrical input power at its point of optimum energy efficiency, where ηtarget is the output value from the appropriate equation in Section 3 of Annex II, using the applicable integer N of the efficiency grade (Annex I, Section 2, Tables 1 and 2) and the electrical power input Pe(d) of the fan expressed in kW at its point of optimum energy efficiency in the applicable energy efficiency formula. | (18) The ‘minimum fan efficiency’ (ηmin) is the fan efficiency to be achieved in order to meet the requirements, calculated as the outcome of the appropriate equation in Annex II, Table 1, using the applicable integer N of the efficiency grade and the electrical power input Pe of the fan expressed in kW at its bep.

## Slide 56: Annex I considerations for definitions
‘Efficiency grade’ implicitly refers to the FMEG (Fan and Motor Efficiency Grades) according to ISO 12759, but –given also the criticism in the SH meeting (harsh for small, lenient for big fans)– it need not necessarily refer to that; it could just be a self-standing parameter.
‘minimum fan efficiency’ is the normal term. In many ED regulations it is not even part of the definitions

## Slide 57: Annex I (old 16-17 eliminated)
(16) ‘Variable speed drive (VSD)’ means an electronic power converter integrated — or functioning as one system — with the motor and the fan, that continuously adapts the electrical power supplied to the electric motor in order to control the mechanical power output of the motor according to the torque-speed characteristic of the load being driven by the motor, excluding variable voltage controllers where only the supply voltage for the motor is varied. |  Moved to Art. 2 (& extended)
(17) ‘Overall efficiency’ is either ‘static efficiency’ or ‘total efficiency’, whichever is applicable. |  Not used (eliminated)

## Slide 58: Annex I (19)
new | (19) 'test fan' is the fan, as defined in Article 2, whereby for the purpose of compliance testing the manufacturer must add motor or bearing struts and, except for jet fans, an orifice panel or orifice ring, to which said struts are attached for the benefit of testing, may remove the parts and geometry sections, e.g. in case the envelope extends beyond the defined inlet and outlet sections, that are not included in the defined stator, may conduct the tests with the geometrical equivalent of the stator inner surface, may conduct the tests with a scale model and calculate the results for the real-size product if the latter has an impeller diameter above 1 m for jet fans or 0,5 m for other fans, may conduct the tests at customer's or manufacturer's site if the latter has an impeller diameter above 1 m for jet fans or 0,5 m for other fans, provided that reliable, accurate and reproducible test- and calculation methods are used and modifications, test conditions and calculations are meticulously reported as prescribed in Annex I, section 3.

## Slide 59: Annex I considerations for definitions
The wording of this part needs to be further discussed in an expert group. The intention is a) always to be able to get test results (no excusesloopholes) and b) to use the latest insights (Uni Darmstadt) in scaling up technology.
Comment industry: The limit should not be 0,5 m, but 1,6 m diameter before scaling etc. can be used.

## Slide 60: Annex I (20)
following ISO 5801  | (20) 'test gas' is the working fluid for the purpose of compliance testing, and independent of the actual gas used in the fan, is clean air at standard inlet conditions of 20 °C and 10325 Pa.

## Slide 61: Annex II (previously Annex I.2) Efficiency Requirements
Commission Regulation 327/2011 | Proposed change (Explanation see text)
2. Fan energy efficiency requirements | 2. Fan energy efficiency requirements
Table 1.See discussion later | Table 1.See discussion later

## Slide 62: Annex II.2 (in discussion doc. at end of Annex III)
2. Measurement method | 
For the purposes of compliance and verification of compliance with the requirements of this Regulation, measurements and calculations must be made using a reliable, accurate and reproducible method, which takes into account the generally recognised state-of-the-art measurement methods, and whose results are deemed to be of low uncertainty, including methods set out in documents the reference numbers of which have been published for that purpose in the Official Journal of the European Union. | For the purposes of compliance and verification of compliance with the requirements of this Regulation, measurements and calculations must be made using a reliable, accurate and reproducible method, which takes into account the generally recognised state-of-the-art measurement methods, and whose results are deemed to be of low uncertainty, including methods set out in documents the reference numbers of which have been published for that purpose in the Official Journal of the European Union.

## Slide 63: Structure
Regulation main text (5 p.)
Annex I: Ecodesign requirements (4 p.)
Annex II: Measurements and calculations (3 p.)
Annex IV: Verification procedure (1 p.)
Annex V: Benchmarks (1 p.)
TOTAL 14 pages (Word)
Regulation main text (4 or 5 p.)
Annex I: Definitions (1-2 p.)
Annex II: Ecodesign requirements (1 p.)
Annex III: Product information requirements (1 p.)
Annex IV: Verification procedure (1 p.)
Annex V: Benchmarks (1 p.)
TOTAL 10-11 pages (Word)
25 - 30% reduction

## Slide 64: Requirements
Annex II.1 Revisited

## Slide 65: Current requirements 327/2011
Fan types | Measure-ment category (A-D) | Efficiency category (static or total) | Power range P in kW | Target energy efficiency (*%) | Efficiency grade (N, *%) | 
 |  |  |  |  | 1.1.2013 | 1.1.2015
Axial (AX) | A, C | static | 0,125 ≤ P ≤ 10 | ηtarget = 2,74 · ln(P) – 6,33 + N | 36 | 40
 |  |  | 10 < P ≤ 500 | ηtarget = 0,78 · ln(P) – 1,88 + N |  | 
 | B, D | total | 0,125 ≤ P ≤ 10 | ηtarget = 2,74 · ln(P) – 6,33 + N | 50 | 58
 |  |  | 10 < P ≤ 500 | ηtarget = 0,78 · ln(P) – 1,88 + N |  | 
Centrifugal FC | A, C | static | 0,125 ≤ P ≤ 10 | ηtarget = 2,74 · ln(P) – 6,33 + N | 37 | 44
 |  |  | 10 < P ≤ 500 | ηtarget = 0,78 · ln(P) – 1,88 + N |  | 
 | B, D | total | 0,125 ≤ P ≤ 10 | ηtarget = 2,74 · ln(P) – 6,33 + N | 42 | 49
 |  |  | 10 < P ≤ 500 | ηtarget = 0,78 · ln(P) – 1,88 + N |  | 
Centrifugal BC without h. (BC0) | A, C | static | 0,125 ≤ P ≤ 10 | ηtarget = 4,56 · ln(P) – 10,5 + N | 58 | 62
 |  |  | 10 < P ≤ 500 | ηtarget = 1,1 · ln(P) – 2,6 + N |  | 
Centrifugal BC with housing (BC1) | A, C | static | 0,125 ≤ P ≤ 10 | ηtarget = 4,56 · ln(P) – 10,5 + N | 58 | 61
 |  |  | 10 < P ≤ 500 | ηtarget = 1,1 · ln(P) – 2,6 + N |  | 
 | B, D | total | 0,125 ≤ P ≤ 10 | ηtarget = 4,56 · ln(P) – 10,5 + N | 61 | 64
 |  |  | 10 < P ≤ 500 | ηtarget = 1,1 · ln(P) – 2,6 + N |  | 
Mixed flow (MF) | A, C | static | 0,125 ≤ P ≤ 10 | ηtarget = 4,56 · ln(P) – 10,5 + N | 47 | 50
 |  |  | 10 < P ≤ 500 | ηtarget = 1,1 · ln(P) – 2,6 + N |  | 
 | B, D | total | 0,125 ≤ P ≤ 10 | ηtarget = 4,56 · ln(P) – 10,5 + N | 58 | 62
 |  |  | 10 < P ≤ 500 | ηtarget = 1,1 · ln(P) – 2,6 + N |  | 
Cross flow (CF) | B, D | total | 0,125 ≤ P ≤ 10 | ηtarget = 1,14 · ln(P) – 2,6 + N | 13 | 21
 |  |  | 10 < P ≤ 500 | ηtarget = N |  | 

## Slide 66: Discussion document requirements (Nov.’14)
Axial fans |  |  |  |  |  |  | 
Efficiency category (measurem. category) | N2018 per 1.1.’18 | N2020 per 1.1.’20 | ηmin at Pe≤1 kW | ηmin at 1kW<Pe≤200 kW |  |  | ηmin at Pe>200 kW
static (A, C) | 44% | 48% | (3.8%+0.5(N-N2018)) *LN(P)-7.4%+N | 3.8%*LN(P)-7.4%+N |  |  | 3.8%*LN(200) -7.4%+N
jet(A) | 53% | 57% |  |  |  |  | 
total (B, D) | 62% | 66% |  |  |  |  | 
Mixed flow fans |  |  |  | 1kW<Pe<10 kW |  | 10kW<Pe<200 kW | 
static (A, C) | 54% | 58% | (5%+0.5(N-N2018)) *LN(P)-8.7%+N | 5%*LN(P) -8.7%+N | 3.4%*LN(P) -5.1%+N |  | 3.4%*LN(200) -5.1%+N
total (B,D) | 64% | 68% |  |  |  |  | 
Centrifugal fans |  |  |  |  |  |  | 
static (A, C) | 64% | 68% | (6.2%+0.5(N-N2018)) *LN(P)-10%+N | 6.2%*LN(P) -10%+N | 3%*LN(P) -2.8%+N |  | 3%*LN(200) -2.8%+N
total (B,D) | 67% | 70% |  |  |  |  | 
Cross flow fans |  |  |  |  |  |  | 
total (B,D) | 21% | 21% | N |  |  |  | 

## Slide 67: Industry (highest values)
Pe | ηmin for all types |  |  | 
0.125 ≤ Pe ≤ 10 | ηmin= 4.56*LN(Pe)-10.5+N |  |  | 
Pe > 10 | ηmin= 1.1*LN(Pe)-2.6+N |  |  | 
 | N Reg 327/2011 | N Industry | N increment | New curve
 | 2015 | 2020 |  | 
AX static (cat. A,C) | 40 | 50 | +10 | BC curve
AX total | 58 | 64 | +4 (static+14) | BC curve
FC static | 44 | 52 | +8 | BC curve
FC total | 49 | 57 | +8 (static+5) | BC curve
BC static | 62 | 64 | +2 (EVIA 0) | 
BC total | 64 | 67 | +3 (static+3) | 
MF static | 50 | 57 | +5 | 
MF total | 62 | 67 | +3 (static+10) | 
CF total | 21 | 21 | 0 | 
BC no housing | combined with BC housing (consensus) |  |  | 
FC | opinion divided to have separate category |  |  | 
2018 tier | consensus against (design cycle minimum 4-5 years) |  |  | 
Discussion doc. | too ambitious (negative impact on SMEs) |  |  | 

## Slide 74: Formulas, Basics(discussion doc ANNEX)
Consistency with current fan regulation and (draft) regulations motors/pumps/circulators/ventilation units/compressors/hoods
Especially consistency scope with draft motor regulation (requested at 1st SH meeting):
  Motor 120 W-1000 kW motor output.
  Fans 125 W – 500 kW electric input
  Means: 125 – 200 W electric input covered by fan but not motor regulation. 500-1000 kW not covered by fan, but by motor regulation.
  SH comments (Apr.-Nov.’24): current regulation stringent for small fans and lenient for large fans
  No industry database, but use anecdotal data from manufacturer catalogues

## Slide 75: Formulas, Guiding principles I (discussion doc ANNEX)
Keep small fan (125W pivot) values close to 2015 level. Set new anchor for slope-change at 1 kW (follows from available data, also LN(1)=0)
Keep 10 kW limit as anchor for slope-change (consistency, but VU uses 30 kW..)
Slopes for medium/large fans to be based on anecdotal data, but keep close to ‘efficiency grade’ and log-dependence of current formulas (better transition/communication/consistency)
Current regulation gives 4% jump between 2013 and 2015  same for 2015-2018 and 2018-2020
Technical logic for centrifugal fans: Fan limits should be between ‘motor’ and ‘ventilation unit’ regulation. Fan limits > Compressor limits.
Manufacturer’s catalogues: Measurement category A (free inlet & outlet, static pressure) is by far the most popular, so this is basis for curve fitting

## Slide 76: Formulas, Guiding principles II(discussion doc ANNEX)
Category logic:
  Cross flow: No anecdotal data found to confirm even the 21% level keep 2015 level at N=21% (2013 level at N=13% would even be better).
  Centrifugal FC: Category not needed (technically but not functionally different from BC; allowing lower limits  no level playing field)
  Centrifugal BC: Distinction with/without housing not needed (for simplification: only 1-2% difference)
  Mixed flow: Straight average between centrifugal and axial
  Axial fans: Benchmark values (Annex V) show that there is relatively more room for higher limits than with centrifugal fans
  Jet fans: are axial (or centrifugal) fans, but with different functionality: creating dynamic pressure (thrust) is the main objective.  different test method.

## Slide 77: Centrifugal, 0.125-1kW, slope (from anecdotal EU industry data)

## Slide 78: Centrifugal fans 0.125-1kW versus draft motor and ventilation unit regulation

## Slide 79: Centrifugal fans 0.125-10 kW versus draft motor and ventilation unit regulation

## Slide 80: Centrifugal fans 0.125-500 kW versus draft motor and ventilation unit regulation

## Slide 81: Centrifugal fans 0.125-500 kW versus draft motor and ventilation unit regulation

## Slide 82: Centrifugal fans 0.125-500 kW versus draft compressor regulation

## Slide 83: Range hood FDE versus fan efficiencies

## Slide 84: Axial jet fan average (dynamic) efficiency

## Slide 85: Axial jet fan average (dynamic) efficiency

## Slide 86: Axial fan, 0.125-1 kW, data slope

## Slide 87: Axial fan, 0.125-1 kW, efficiencies

## Slide 88: Axial fan, up to 10 kW

## Slide 89: Axial fan, up to 100 kW

## Slide 90: Annex III.1, III.2 (previously Annex I.3) Product information (1 – 6)
3. Product information requirements on fans | 3. Product information requirements on fans
1. The information on fans set out in points 2(1) to 2(14) shall be visibly displayed on: | 1. The information on fans set out in points 2(1) to 2(14) shall be visibly displayed on:
(a) the technical documentation of fans; | (a) the technical documentation of fans;
(b) free access websites of manufacturers of fans. | (b) free access websites of manufacturers of fans.
2. The following information shall be displayed: | 2. The following information shall be displayed:
(1) overall efficiency (η), rounded to 1 decimal place; | (1) overall efficiency (η) rounded to 3 decimal places;
(2) measurement category used to determine the energy efficiency (A-D); | (2) measurement category used to determine the energy efficiency (A-D);
(3) efficiency category (static or total); | (3) efficiency category (static or total);
(4) efficiency grade at optimum energy efficiency point; | (4) efficiency grade at bep;
(5) whether the calculation of fan efficiency assumed use of a VSD and if so, whether the VSD is integrated within the fan or the VSD must be installed with the fan; | (5) whether the calculation of fan efficiency assumed use of a VSD and if so, whether the VSD is integrated within the fan or the VSD must be installed with the fan;
(6) year of manufacture; | (6) year of manufacture;

## Slide 91: Annex III.2 (7-14)
(7) manufacturer’s name or trade mark, commercial registration number and place of manufacturer; | (7) manufacturer’s name or trade mark, commercial registration number and place of manufacturer;
(8) product’s model number; | (8) product’s model number;
(9) the rated motor power input(s) (kW), flow rate(s) and pressure(s) at optimum energy efficiency; | (9) the electric motor power input (kW), flow rate (in m³/h integer values when <1 m³/s, else in m³/s with 2 digit precision) and applicable pressure difference (in Pa) at bep;
(10) rotations per minute at the optimum energy efficiency point; | (10) rotations per minute at bep;
(11) the ‘specific ratio’; | (11) the ‘specific ratio’;
(12) information relevant for facilitating disassembly, recycling or disposal at end-of-life; | (12) information relevant for facilitating disassembly, recycling or disposal at end-of-life;
(13) information relevant to minimise impact on the environment and ensure optimal life expectancy as regards installation, use and maintenance of the fan; | (13) information relevant to minimise impact on the environment and ensure optimal life expectancy as regards installation, use and maintenance of the fan;
(14) description of additional items used when determining the fan energy efficiency, such as ducts, that are not described in the measurement category and not supplied with the fan. | (14) description of additional items used when determining the fan energy efficiency, such as ducts, that are not described in the measurement category and not supplied with the fan.
3. The information in the technical documentation shall be provided in the order as presented in points 2(1) to 2(14).The exact wording used in the list does not need to be repeated. It may be displayed using graphs, figures or symbols rather than text. | 3. The information in the technical documentation shall be provided in the order as presented in points 2(1) to 2(14).The exact wording used in the list does not need to be repeated. It may be displayed using graphs, figures or symbols rather than text.

## Slide 92: Annex III.4-5
4. The information referred to in points 2(1), 2(2), 2(3), 2(4) and 2(5) shall be durably marked on or near the rating plate of the fan, where for point 2(5) one of the following forms of words must be used to indicate what is applicable: | 4. The information referred to in points 2(1), 2(2), 2(3), 2(4) and 2(5) shall be durably marked on or near the rating plate of the fan, where for point 2(5) one of the following forms of words must be used to indicate what is applicable:
— ‘A variable speed drive must be installed with this fan’, | — ‘A variable speed drive must be installed with this fan’,
— ‘A variable speed drive is integrated within the fan’. | — ‘A variable speed drive is integrated within the fan’.
5. Manufacturers shall provide information in the manual of instruction on specific precautions to be taken when fans are assembled, installed or maintained. If provision 2(5) of the product information requirements indicates that a VSD must be installed with the fan, manufacturers shall provide details on the characteristics of the VSD to ensure optimal use after assembly. | 5. Manufacturers shall provide information in the manual of instruction on specific precautions to be taken when fans are assembled, installed or maintained. If provision 2(5) of the product information requirements indicates that a VSD must be installed with the fan, manufacturers shall provide details on the characteristics of the VSD to ensure optimal use after assembly. (still allowed?)

## Slide 93: Annex III considerations for product information
Question: Is it still allowed to claim a VSD bonus, simply by declaring that the fan should be installed with a VSD? The intention was that this bonus should be a compensation, but if the efficiency is established without VSD-losses then there is no reason for this compensation.

## Slide 94: Current Annex II (deleted)
Commission Regulation 327/2011 | Proposed change
ANNEX II | Removed completely (moved to main text and Annex I)
MEASUREMENTS AND CALCULATIONS | Non-final assembly provisions no longer applicable
1. Definitions for the purposes of Annex II | 
Etc….. | 

## Slide 95: Annex IV.1-2 Verification
VERIFICATION PROCEDURE FOR MARKET SURVEILLANCE PURPOSES | VERIFICATION PROCEDURE FOR MARKET SURVEILLANCE PURPOSES
When performing the market surveillance checks referred to in Article 3(2) of Directive 2009/125/EC, the authorities of the Member States shall apply the following verification procedure for the requirements set out in Annex I. | When performing the market surveillance checks referred to in Article 3(2) of Directive 2009/125/EC, the authorities of the Member States shall apply the following verification procedure for the requirements set out in Annex I.
1. The authorities of the Member State shall test one single unit. | 1. The authorities of the Member State shall test one single unit.
2. The model shall be considered to comply with the provisions set out in this Regulation if the overall efficiency of the fan (ηe) is at least target energy efficiency*0,9 calculated using the formulas in Annex II (Section 3) and the applicable efficiency grades from Annex I. | 2. The model shall be considered to comply with the provisions set out in this Regulation if the fan efficiency (ηf) is at least the minimum fan efficiency*0,93 calculated using the formulas in Annex II (Section 1) and the applicable efficiency grades.

## Slide 96: Annex IV.3-5
3. If the result referred to in point 2 is not achieved: | 3. If the result referred to in point 2 is not achieved:
— for models that are produced in lower quantities than five per year, the model shall be considered not to comply with this Regulation, | — for models that are produced in lower quantities than five per year, the model shall be considered not to comply with this Regulation,
— for models that are produced in quantities of five or more per year, the market surveillance authority shall randomly test three additional units. | — for models that are produced in quantities of five or more per year, the market surveillance authority shall randomly test three additional units.
4. The model shall be considered to comply with the provisions set out in this Regulation if the average of the overall efficiency (ηe) of the three units referred to in point 3 is at least target energy efficiency*0,9 using the formulas in Annex II (Section 3) and the applicable efficiency grades from Annex I. | 4. The model shall be considered to comply with the provisions set out in this Regulation if the average of the overall efficiency (ηe) of the three units referred to in point 3 is at least the minimum fan efficiency*0,93 using the formulas in Annex II (Section 1) and the applicable efficiency grades.
5. If the results referred to in point 4 are not achieved, the model shall be considered not to comply with this Regulation. | 5. If the results referred to in point 4 are not achieved, the model shall be considered not to comply with this Regulation.

## Slide 97: Annex IV considerations for verification procedure
7% deviation from the declared value is the same as for ventilation units (which are even more complex to test).

## Slide 98: Annex V (previously IV): Benchmarks
ANNEX IV (current 327/2011, new values to be discussed) |  |  | 
INDICATIVE BENCHMARKS REFERRED TO IN ARTICLE 6 |  |  | 
At the time of adoption of this Regulation, the best available technology on the market for fans is as indicated in Table 1. These benchmarks may not always be achievable in all applications or for the full power range covered by the Regulation. |  |  | 
Table 1 |  |  | 
Indicative benchmarks for fans |  |  | 
Fan types | Measurement category (A-D) | Efficiency category (static or total) | Efficiency grade
Axial fan | A, C | static | 65
 | B, D | total | 75
Centrifugal forward curved fan and centrifugal radial bladed fan | A, C | static | 62
 | B, D | total | 65
Centrifugal backward curved fan without housing | A, C | static | 70
Centrifugal backward curved fan with housing | A, C | static | 72
 | B, D | total | 75
Mixed flow fan | A, C | static | 61
 | B, D | total | 65
Cross flow fan | B, D | total | 32

## Slide 101
Excluding FC

## Slide 102
Excluding FC

## Slide 103: Slides 1 Oct. 2014 (1st SH meeting)

## Slide 104: 8.2. Ecodesign requirements (2/4)
Graph by: Harry Keller, Helios Ventilatoren GmbH
0.10
0.08
0.04
0.06

## Slide 105: Other issues - sales
sales (based on prep.study)
Fan type | sales [mio units] |  |  |  |  |  | 
 | 1995 | 2000 | 2005 | 2010 | 2015 | 2020 | 2025
Axial<300Pa | 0.9 | 2.25 | 2.4 | 2.62 | 3 | 3.39 | 3.78
Axial>300Pa | 0.93 | 2.51 | 2.7 | 2.86 | 3.01 | 3.17 | 3.33
Centr.FC | 0.46 | 0.66 | 1.12 | 1.04 | 1.2 | 1.36 | 1.52
Centr.BC/no housing | 0.14 | 0.21 | 0.33 | 0.31 | 0.35 | 0.39 | 0.43
Centr.BC | 0.14 | 0.23 | 0.37 | 0.34 | 0.39 | 0.44 | 0.49
Cross-flow | 0.13 | 0.23 | 0.19 | 0.26 | 0.3 | 0.34 | 0.37
Box | 1.53 | 2.58 | 2.3 | 2.91 | 3.13 | 3.35 | 3.57
Roof_all | 1.99 | 3.87 | 3.4 | 4.1 | 4.33 | 4.55 | 4.78
TOTAL | 6.23 | 12.54 | 12.81 | 14.44 | 15.72 | 16.99 | 18.27
for stock / installed base: lifetime assumed is 15 yrs

## Slide 106: Increasing levels (repeat slides)

## Slide 111
Excluding FC

## Slide 116
Excluding FC